## DEMAND WORKSHEET
(REVISED 08/29/2024)
SUBDIVISION (If Applicable):
DEVELOPER/BUILDER:
LOT # (If Applicable):
ADDRESS:
CITY:
Typical Flow Rates for Appliances and Fixtures
*(Fill out information in "yellow" cells)*- INFORMATION IS FOR SERVICES SMALLER THAN 3"
Fixture/Appliance | Flow Range (gpm) |  | Total number of each fixture in building | *Flow Range (GPM) required.
| Min. | Max.
Kitchen faucet | 2 | 3 | 0 | 0
Bar faucet | 2 | 2.5 | 0 | 0
Bathroom faucet | 2.5 | 2.5 | 0 | 0
Bathtub Faucet/ Shower head combo | 1.5 | 3 | 0 | 0
Toilet, 1.6 GPF gravity tank | 2 | 3 | 0 | 0
Washing machine | 3 | 5 | 0 | 0
Laundry Sink faucet | 2 | 3 | 0 | 0
Dishwasher | 2 | 3.5 | 0 | 0
Hose bib | 3 | 3 | 0 | 0
Roman Tub Faucet | 12 | 16 | 0 | 0
Irrigation system | 13 | 15 | 0 | 0
*Service Sink Faucet/Mop Sink | 3 | 5 | 0 | 0
* Drinking Fountain | 0.75 | 1 | 0 | 0
*Toilet, 1.6 GPF Flushometer Valve | 2 | 2.5 | 0 | 0 | Click here for a definition for this fixture
*Toilet, >1.6 GPF Flushometer Valve | 3 | 4 | 0 | 0 | Click here for a definition for this fixture
*Urinal, 1.0 GPF | 0.5 | 1 | 0 | 0 | Click here for a definition for this fixture
*Urinal, >1.0 GPF | 1 | 3 | 0 | 0 | Click here for a definition for this fixture
* Typically not used in residential applications
| Total fixture flow rate: |  |  | 0
Total GPM request based on 50% fixture operation W/O Roman tub or Lawn irrigation |  |  |  | 0 | GPM
Total GPM request based on 25% % fixture operation while Roman tub in operation |  |  |  | 0 | GPM
Total GPM request based on 25% % fixture operation while lawn irrigation in operation |  |  |  | 0 | GPM
Highest flow demand required |  |  |  | 0 | GPM
Pressure at outlet
Minimum static pressure at service request location |  |  |  | 0 | PSI |  | side of meter
Length of service line (Water Main to Meter Box) |  |  |  | 0 | Feet |  | (=>40 PSI)
1" copper service line pressure loss |  |  |  | 0 | PSI
3/4" meter pressure loss |  |  |  | FALSE | PSI | DO NOT USE | 0 | PSI
1" copper service line pressure loss |  |  |  | 0 | PSI
1" meter pressure loss |  |  |  | FALSE | PSI | DO NOT USE | 0 | PSI
1 1/2" copper service line pressure loss |  |  |  | 0 | PSI
3/4" meter pressure loss |  |  |  | FALSE | PSI | DO NOT USE | 0 | PSI
1 1/2" copper service line pressure loss |  |  |  | 0 | PSI
1" meter pressure loss |  |  |  | FALSE | PSI | DO NOT USE | 0 | PSI
1 1/2" copper service line pressure loss |  |  |  | 0 | PSI
1 1/2" meter pressure loss |  |  |  | FALSE | PSI | DO NOT USE | 0 | PSI
2" copper service line pressure loss |  |  |  | 0 | PSI
1" meter pressure loss |  |  |  | FALSE | PSI | DO NOT USE | 0 | PSI
2" copper service line pressure loss |  |  |  | 0 | PSI
1 1/2" meter pressure loss |  |  |  | FALSE | PSI | DO NOT USE | 0 | PSI
2" copper service line pressure loss |  |  |  | 0 | PSI
2" meter pressure loss |  |  |  | FALSE | PSI | DO NOT USE | 0 | PSI
2 1/2" copper service line pressure loss |  |  |  | 0 | PSI
1" meter pressure loss |  |  |  | FALSE | PSI | DO NOT USE | 0 | PSI
2 1/2" copper service line pressure loss |  |  |  | 0 | PSI
1 1/2" meter pressure loss |  |  |  | FALSE | PSI | DO NOT USE | 0 | PSI
2 1/2" copper service line pressure loss |  |  |  | 0 | PSI
2" meter pressure loss |  |  |  | FALSE | PSI | DO NOT USE | 0 | PSI
Notes:
GPM= Gallons Per Minute
* Calculations use "Max" GPM requirement
Flow Range for fixtures compiled from USEPA, AWWA, and other sources.
Flow rates for various fixtures/appliances may vary by manufacture.
Toilet flow rates are for less than 1 minute duration based on 1.6 gallon per flush standards
Dishwasher flow rates are for approximately 1 minute duration based on efficiency standards and typical usage of 5 to 8 gallons per load
Irrigation flow rate provided by lawn irrigation company as average.
Note on G27: A 1.6 GPF water closet is a typical tank\bowl toliet made AFTER 1992 that uses a pressure vessel, not gravity
Note on G28: A >1.6 GPF water closet is a typical tank\bowl toliet made BEFORE 1992 or rated as such that uses a pressure vessel, not gravity
Note on G29: A 1.0 GPF urinal are those urinals made AFTER 1992.Urinals are not common in residential houses
Note on G30: A >1.0 GPF urinal are those urinals made BEFORE 1992. Urinals are not common in residential houses

## NEW SERVICE APPLICATION
MISSOURI-AMERICAN WATER COMPANY
NEW SERVICE APPLICATION
I AM APPLYING FOR:
| Domestic Service |  |  |  | Fire Service |  |  |  | Irrigation Service
SERVICE LOCATION:
Street Address |  | 0 |  |  |  |  | City |  | 0
County |  |  |  |  | Subdivision | 0 |  |  |  | Lot | 0
Developer / Builder |  |  | 0
Property is situated between Streets | [7 empty] | &
*Please place an "X" in your preferred service location in the "Yellow" box in the below diagram:
BUILDING
APPLICANT INFORMATION:
Name
Address | [8 empty] | City
Phone |  |  | Cell |  |  | Email
BILLING INFORMATION (Party Responsible for Bill):
Name
Address | [8 empty] | City
Phone |  |  | Cell |  |  | Email
BILLING POINT OF CONTACT INFORMATION (If an Organization):
Name
Phone |  |  | Cell |  |  | Email
Missouri-American Water Company
New Service Application
Page 1 of 3
MISSOURI-AMERICAN WATER COMPANY
NEW SERVICE APPLICATION
THIS PROPERTY IS:
| New Construction |  |  |  | Subdivision |  |  |  | Vacant Land
| Existing Building |  |  |  | Demolition |  |  |  | Currently Using Well Water
USE OF SERVICE:
| Single Family |  |  |  | Commecial
| Multi-Family (2-4 Units) |  |  |  | Irrigation Only
| Apartments (5 Unit and Up) |  |  |  | Other (Describe)
COMPLETE FOR DOMESTIC WATER SERVICE
(Provide MAWC Demand Worksheet-Indicate Service Line and Meter Size below from worksheet)
Is there an exisitng domestic |  |  |  |  | Yes |  |  |  | No
service at the property?
If "Yes" do you want to : |  |  |  |  | Replace / Upgrade |  |  |  | Add a new service
[5 empty] | the exisitng service |  |  |  | (Keep the Existing Service)
What size service line are you requesting? | [5 empty] | (Information taken from Demand Worksheet
What size meter are you requesitng? | [5 empty] | this applies to services smaller than 3")
COMPLETE FOR FIRE SERVICE
Is there an existing fire service |  |  |  |  | Yes |  |  |  | No
at the property?
If "Yes" do you want to : |  |  |  |  | Replace / Upgrade |  |  |  | Add a new service
[5 empty] | the exisitng service |  |  |  | (Keep the Existing Service)
What size fire service are you requesting?
Please attach the executed "Application for Special Connection" form to this application.
Sprinkler plans must be submitted / reviewed and acknowledged by the local fire official,
who should sign the "Application for Special Connection form that they have seen the plans.
COMPLETE FOR IRRIGATION SERVICE
What size meter are you requesting ? | [5 empty] | What is your gallons per minute (GPM)
requirement?
What size irrigation service are you requesting?
Missouri-American Water Company
New Service Application
Page 2 of 3
MISSOURI-AMERICAN WATER COMPANY
NEW SERVICE APPLICATION
APPLICANT, PLEASE COMPLETE AND SIGN BELOW:
I understand that these services are subject to the rates and conditions of Missouri American
Water Company.
I understand that I will be billed for water usage on fire services for purposes other than fire
suppression / extinguishment or testing and that it is encouraged that customers notify the water
company's local office after the fire service is used for such purposes.
I understand that it is the applicant's and/ or their agent's responsibility to ensure their plumbing
system is in compliance with all applicable code requirements.
I understand that a Backflow Device that meets jurisdictional requirements is required for all fire
services and on domestic service were potential cross conneciton may occur.
Existing Well, if any, will be physically removed.
Is there a Plumbing Contractor/ |  |  |  |  | Yes |  |  |  | No
Fire Sprinkler Contractor
Applicant wishes to utilize and
"Sole Source " bidding ?
If "Yes" Please provide Contractors name:
Print Name: | [6 empty] | Title:
Signature: | [6 empty] | Date:
Missouri-American Water Company
New Service Application
Page 3 of 3
Note on P159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PRESS THE "CTRL" BUTTON AND THE SEMI-COLON BUTTON ";" AT THE SAME TIME TO POPULATE CURRENT DATE.

## NEW SERVICE BID SHEET
MISSOURI-AMERICAN WATER COMPANY
DISTRICT: ST. LOUIS COUNTY, MO
PRICE SCHEDULE
CONTRACTOR NAME: | 0
SUBDIVISION: | 0
DEVELOPER/BUILDER: | 0
LOT #: | 0
ADDRESS: | 0
NEW SERVICE LINES AND METER SETTING INSTALLATIONS
NOTES:
Must include LEAD FREE FITTINGS
Except where the Company elects to furnish materials for the jobs assigned to Contractor, Contractor will furnish at its expense all materials necessary for use in the job assigned to it.
Contractor will be responsible for hauling materials furnished by Company from the Company's point of supply to the job. Contractor will furnish all materials (except that supplied by the Company), tools, equipment and labor necessary for the proper completion of the jobs assigned to Contractor.
The Contractor will have two working weeks from time of transmittal to complete installation of new service unless other arrangements are agreed upon with owner. During times of inclement weather, OWNER and Contractor will agree upon a completion date.
All Restoration will be the at the sole costs and resposibility of the Developer/ Requestor of the new service installation.
Contractor will render invoices detailing date, location, materials, and type of work completed. Contractor will also attach to such monthly invoice written proof satisfactory to Company that no such employee and no material person or supplier or any person has any lien or claim on the work or against the Company
because of the work for which compensation is sought. Contractor to detail all applicable taxes on invoice as a separate line item for all materials provided by contractor. Contractor must identify each location and breakout all charges for individual addresses. Invoices will need to be broken out by Labor, Material, Paving and Restoration.
A Purchase Order will be issued in order to submit invoices against.
All materials shall be purchased from Core & Main , Midwest Municipal or Plumbers Supply.
Contractor Safety Brief to be reviewed and signed off by all employees that perform work.
Service installation shall include excavation of tap hole. MOAW will make the tap, provide the saddle (if applicable), corp, tail piece.
Contractor responsible for obtaining all Permits. Permitting/Escrow Bonds shall not be included in pricing and will be a pass through cost.
Meter Setter shall include Locking Arrow Inlet valve and Check valve on outlet side of setter. Price shall include all fittings, bushings, adapters and meter setter support for proper installation. ** Plumbing Contractor to leave meter adapter fititngs in the meter pit for meter installation. **
*Contractor shall not call MAWC for tap until all contractor installed service and meter setter and box are installed.*
Contractor as part of this bid sheet will connect service installation to the previously installed customer side of the service.
PLEASE PROVIDE PRICE FOR SELECTED SERVICE TYPE BELOW:
Place "X" in area to provide price
Type of Service | 1" Service - 3/4" Meter |  | 1"Service - 1" Meter |  | 1-1/2" Service -3/4" meter |  | 1-1/2" Service - 1" meter |  | 1-1/2" Service - 1 1/2" meter |  | 2" Service - 1" meter |  | 2" Service - 1 1/2" meter |  | 2" Service - 2" meter |  | 2-1/2" Service - 1" meter |  | 2-1/2" Service - 1 1/2" meter |  | 2-1/2" Service - 2" meter
| 1" Copper Service Line, from 1" corp, enter meter box with 1" service line to (1") locking inlet valve, 3/4" yoke bar for installation of (3/4") meter, includes necessary fittings and adapters, (1") check valve outlet side of setter, (1") service line exiting the meter box 4', 24" Meter Box, adapter ring and 12" composite cover per spec. |  | 1" Copper Service Line, from 1" corp, enter meter box with (1") service line to (1") locking inlet valve, 1" yoke bar for (1") meter installation and necessary fittings/ bushings, (1") check valve outlet side of setter, (1") service line exiting the box 4', 24" Meter Box, adapter ring and 12" composite cover per spec. |  | 1-1/2" Copper Service Line, from 2-1" corps into (1") fingers into manifold, enter box with (1 1/2") service line and reduce to (1") copper into a 3/4" yoke bar for installation of (3/4") meter that includes (1") locking inlet valve, Appropriate adapters for (3/4") meter yoke bar installation, (1") check valve outlet side of setter, includes all bushings and fittings, (1 1/2") service line exiting the box 4', 24" Meter Box, adapter ring and 12" composite cover per spec. |  | 1-1/2" Copper Service Line, from 2-1" corps into (1") fingers into manifold, enter box with (1 1/2") service line and reduce to (1") copper into a 1" yoke bar for installation of (1") meter that includes (1") locking inlet valve, (1") check valve outlet side of setter, includes all bushings and fittings, (1 1/2") service line exiting the box 4',24" Meter Box, adapter ring and 12" composite cover per spec. |  | 1-1/2" Copper Service Line, from 2-1" corps into (1") fingers into manifold, enter box with (1 1/2") service line to full (2") copper setter with appropriate adapters for installation of (1 1/2") meter w/1-1/4" high offset bypass on setter , includes (2") locking inlet valve and (2") Check valve Outlet side of setter. (1 1/2") service line exiting the box 4' includes all bushings and fititngs, Meter box to be Old Castle Model# 3660-36 DL/LW flush cover per spec. |  | 2" Copper Service Line, from 2-1" corps into (1") fingers into manifold, enter box with (2") service line and reduce to (1") copper into a (1") yoke bar for installation of (1") meter that includes (1") locking inlet valve, (1") check valve outlet side of setter, includes all bushings and fittings, (2") service line exiting the box 4', 24" Meter Box, adapter ring and 12" composite cover per spec. |  | 2" Copper Service Line, from 2-1" corps into (1") fingers into manifold, enter box with (2") service line to full (2") copper setter with appropriate adapters for installation of (1 1/2") meter w/1-1/4" high offset bypass on setter , includes (2") locking inlet valve and (2") Check valve Outlet side of setter. (2") service line exiting the box 4' includes all bushings and fititngs, Meter box to be Old Castle Model# 3660-36 DL/LW flush cover per spec. |  | 2" Copper Service Line, from 2-1" corps into (1") fingers into manifold, enter box with (2") service line to full (2") copper setter for installation of (2") meter w/1-1/4" high offset bypass on setter , includes (2") locking inlet valve and (2") Check valve Outlet side of setter. (2") service line exiting the box 4' includes all bushings and fititngs, Meter box to be Old Castle Model# 3660-36 DL/LW flush cover per spec. |  | 2 1/2" Copper Service Line, from 2-1" corps into (1") fingers into manifold, enter box with (2 1/2") service line and reduce to (1") copper into a (1") yoke bar for installation of (1") meter that includes (1") locking inlet valve, (1") check valve outlet side of setter, includes all bushings and fittings, (2 1/2") service line exiting the box 4',24" Meter Box, adapter ring and 12" composite cover per spec. |  | 2 1/2" Copper Service Line, from 2-1" corps into (1") fingers into manifold, enter box with (2 1/2") service line reduce to 2" copper to full (2") copper setter with appropriate adapters for installation of (1 1/2") meter w/1-1/4" high offset bypass on setter , includes (2") locking inlet valve and (2") Check valve Outlet side of setter. (2 1/2") service line exiting the box 4' includes all bushings and fititngs, Meter box to be Old Castle Model# 3660-36 DL/LW flush cover per spec. |  | 2 1/2" Copper Service Line, from 2-1" corps into (1") fingers into manifold, enter box with (2 1/2") service line and reduce to 2" copper into a full (2") copper setter for installation of (2") meter w/1-1/4" high offset bypass on setter , includes (2") locking inlet valve and (2") Check valve Outlet side of setter. (2 1/2") service line exiting the box 4' includes all bushings and fititngs, Meter box to be Old Castle Model# 3660-36 DL/LW flush cover per spec.
| LABOR RATE | MATERIAL COSTS | LABOR RATE | MATERIAL COSTS | LABOR RATE | MATERIAL COSTS | LABOR RATE | MATERIAL COSTS | LABOR RATE | MATERIAL COSTS | LABOR RATE | MATERIAL COSTS | LABOR RATE | MATERIAL COSTS | LABOR RATE | MATERIAL COSTS | LABOR RATE | MATERIAL COSTS | LABOR RATE | MATERIAL COSTS | LABOR RATE | MATERIAL COSTS
NEW SERVICE
TOTAL LABOR AND MATERIAL: | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
Notes:
1. Owner and Contractor responsibilities per Agreement
2. Contractor must approve all materials with Owner
3. Price provided will be a costs not to exceed. No extra costs will be paid by Missouri American Water Company.
4. Missouri-American Water Company will make all taps and will supply tapping saddle (If applicable), corp and tail piece.

## TOTAL COSTS SHEET
WATER SERVICE TOTAL COSTS SHEET
MISSOURI-AMERICAN WATER COMPANY
DISTRICT: ST. LOUIS COUNTY, MO
PRICE SCHEDULE
CONTRACTOR NAME: | 0
SUBDIVISION: | 0
DEVELOPER/BUILDER: | 0
LOT #: | 0
ADDRESS: | 0
| Material | Labor
CONTRACTOR BID COSTS | 0 | 0
MAWC-TAP COSTS |  |  | MAWC TO FILL IN TAP COSTS
MAWC-FEE |  | 0
TOTAL COSTS DUE TO MAWC FOR ABOVE REFERENCED WATER SERVICE |  | 0

## METER TABLE (hidden)
Missouri-American Water Company
Residential and small commercial meter sizing
Maximum Instantaneous Flow Rate (GPM) | 5/8" Meter |  | 3/4" Meter |  | 1" Meter |  | 1-1/2" Meter |  | 2" Meter
| Badger Model 25 |  | Badger Model 35 |  | Badger Model 55 |  | Neptune - E-Coder T-10 |  | Neptune - E-Coder T-10
| Pressure Loss Across Meter (PSI) | Minimum Distribution System Pressure Required (PSI) | Pressure Loss Across Meter (PSI) | Minimum Distribution System Pressure Required (PSI) | Pressure Loss Across Meter (PSI) | Minimum Distribution System Pressure Required (PSI) | Pressure Loss Across Meter (PSI) | Minimum Distribution System Pressure Required (PSI) | Pressure Loss Across Meter (PSI) | Minimum Distribution System Pressure Required (PSI) | FAIL
1 | 0 | 40 | 0 | 40 | 0 | 40 | 0 | 40 | 0 | 40
2 | 0 | 40 | 0 | 40 | 0 | 40 | 0 | 40 | 0 | 40
3 | 0.1 | 40.1 | 0.1 | 40.1 | 0 | 40 | 0 | 40 | 0 | 40
4 | 0.2 | 40.2 | 0.2 | 40.2 | 0 | 40 | 0 | 40 | 0 | 40
5 | 0.4 | 40.4 | 0.4 | 40.4 | 0 | 40 | 0 | 40 | 0 | 40
6 | 0.5 | 40.5 | 0.5 | 40.5 | 0.1 | 40.1 | 0 | 40 | 0 | 40
7 | 0.8 | 40.8 | 0.6 | 40.6 | 0.2 | 40.2 | 0 | 40 | 0 | 40
8 | 1 | 41 | 0.7 | 40.7 | 0.2 | 40.2 | 0 | 40 | 0 | 40
9 | 1.2 | 41.2 | 0.8 | 40.8 | 0.3 | 40.3 | 0 | 40 | 0 | 40
10 | 1.5 | 41.5 | 0.9 | 40.9 | 0.3 | 40.3 | 0 | 40 | 0 | 40
15 | 3.5 | 43.5 | 1.6 | 41.6 | 0.5 | 40.5 | 0.2 | 40.2 | 0.1 | 40.1
20 | 6 | 46 | 3.3 | 43.3 | 0.9 | 40.9 | 0.4 | 40.4 | 0.3 | 40.3
30 |  |  | 7.5 | 47.5 | 1.9 | 41.9 | 1 | 41 | 0.6 | 40.6
40 |  |  |  |  | 3.4 | 43.4 | 1.5 | 41.5 | 0.9 | 40.9
50 |  |  |  |  | 5.4 | 45.4 | 2.6 | 42.6 | 1.1 | 41.1
60 | [6 empty] | 3.7 | 43.7 | 1.7 | 41.7
70 | [6 empty] | 4.9 | 44.9 | 2 | 42
80 | [6 empty] | 6.1 | 46.1 | 2.6 | 42.6
90 | [6 empty] | 7.7 | 47.7 | 3.1 | 43.1
100 | [6 empty] | 9.8 | 49.8 | 3.8 | 43.8
110 | [8 empty] | 4.3 | 44.3
120 | [8 empty] | 5.2 | 45.2
130 | [8 empty] | 6.2 | 46.2
140 | [8 empty] | 7.3 | 47.3
150 | [8 empty] | 8.2 | 48.2
160 | [8 empty] | 9.9 | 49.9
| Minimum Pressure After Meter = | 40 | psi

## HEADLOSS CALCULATIONS (hidden)
[12 empty] | Static psi | Res psi
[11 empty] | 1" | 0 | 0
[11 empty] | 1.5" | 0 | 0
[11 empty] | 2" | 0 | 0
[7 empty] | Total pipe | Total hl | Total hl |  | 2.5" | 0 | 0
Pipe diameter (in.) | Area (ft^2) | Flow (gpm) | Flow (cfs) | Vel. (fps) | C factor | hl/100ft (ft.) | length (ft) | (ft.) | (psi) | pipe volume (gal.)
1 | 0.0054542 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0
1.5 | 0.012272 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0
2 | 0.021817 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0
2.5 | 0.034088 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0